ROUTINE TEST RECORD FOR BELT SCALE

JOB No: JOB-2026-886					CUSTOMER NAME: Adani Power Thermal

CAPACITY :	1200             		           CONVEYOR NO : CV-30B

| BELT SCALE | LOAD CELL | SPEED SENSOR | JUNCTION BOX |
| --- | --- | --- | --- |
| Model No: BS-MODEL-886 Serial No: SN-BS-7886 S/W Version: 3.1.3 REMOTE: Model No: RM-UNIT-01 Serial No: SN-RM-5886 | Model No: LC-300KG Serial No: 1) LC1-006 2) LC2-006 3) LC3-006 4) LC4-006 | Model No: TACHO-SENS-PRO Serial No: TS-8886 | Model No: JBOX-IP67 Serial No: JB-SN-986 Model No: JBOX-IP67 Serial No: JB-SN-1086 Model No: JBOX-IP67 Serial No: JB-SN-1186 |
|  |  | ANGLE SENSOR |  |
|  |  | Model No: AS-300-TILT Serial No: SN-AS-9886 |  |

Check for short between Line & Neutral, Neutral & Earth, Line & Earth : OK (Checked Line/Neutral, Neutral/Earth, Line/Earth)

| SL. No. | Test Performed | Specified | Actual |
| --- | --- | --- | --- |
| 1. | Input Supply Voltage (+/-10%) | 230V | 230V |
| 2. | Derived DC Voltages (+/-5%) | 24V | 24V |
| 3. | Display and Keypad Functionality | OK | OK |
| 4. | Belt Load as specified in G.A. or MPL | 170.1 kg/m | 170.1 Kg/m |
| 5. | Belt Speed as specified in G.A. or MPL | 1.96 | 1.96 m/s |
| 6. | Number of PF Contacts | 4 | 4 |
| 7. | Communication Output (Specify) | RS-485 | RS-485 |
| 8. | Analog Output (Specify number) | 4-20mA | 4-20mA |
| 9. | Wiring, TB and Component Layout | OK | OK |

Resolution:            L: 0.1          S: 0.01          r: 1          t: 0.1

Measurement to be done from 0 to 110% of the Belt Scale capacity.

| Load on Load cell Kg/Mv | Belt load Kg/m | Speed in m/s | Rate in tph | Totalizer in Tones (6 min) | O/p current mA AO1 AO2 |  |
| --- | --- | --- | --- | --- | --- | --- |
| 3 | 0.0 | 1.96 | 0 | 0.0 | 4.00 | 4.00 |
| 3 | 34.0 | 1.96 | 240 | 24.0 | 7.20 | 7.20 |
| 4 | 68.0 | 1.96 | 480 | 48.0 | 10.40 | 10.40 |
| 4 | 102.0 | 1.96 | 720 | 72.0 | 13.60 | 13.60 |
| 5 | 136.1 | 1.96 | 960 | 96.0 | 16.80 | 16.80 |
| 5 | 170.1 | 1.96 | 1200 | 120.0 | 20.00 | 20.00 |

Instrument Used: Fluke 87V Digital Multimeter & 50kg Calibrated Class F Weights

Tested by: A				               Approved by: HOD-PDN

Date: 15-Sep-2026					               (HOD - PDN)